[image: image1.jpg]end

energynetworks
association
I

The voice of the networks




EVCP & HP Connections Form v3.3

Cover Page 
Completing this form accurately will help DNOs process your application as quickly as possible. Please read the following information thoroughly before starting to ensure you have all information required to complete the relevant sections.
	What is eligible 
	This form is for Electric Vehicle Charge Points (EVCP) or Heat Pumps (HP) being installed in a premises with an existing Distribution Network Operator (DNO) electricity connection. This form may also be used for the installation of Vehicle-to-Grid Electric Vehicle Charge Points (V2G EVCP) where the total aggregated capacity of generation/battery storage equipment in a premises is 17kW (single phase) or 50kW (3-phase) or less. To apply for a new connection to the network, please contact your relevant DNO.

	When to complete 
	This form should always be reviewed prior to installing any new EVCP or HP to determine whether the installation requires an application or whether it is eligible for the notification process.

	When to submit
	If the installation meets all the notification criteria (Section B) the DNO must be notified within 28 days of installing the new equipment. If all the criteria in Section B cannot be met, you should submit an application to the DNO using this form before connecting the new equipment to ensure that the DNO can maintain safe and effective operation of the electricity network. 

	What to submit
	Depending on the nature of the new equipment, the DNO may require additional information. For multiple pieces of equipment (including multiple pieces of equipment under one controller) or multiple premises, please use the multiple installations spreadsheet, also available on the ENA website
.

	Finding your DNO
	For help identifying your DNO and their contact details please visit the ENA website
.

	Cost
	Any reinforcement costs associated with this installation may be charged to the customer.


Required Information 
To populate this form, you will need information about the following. 

	Device to be installed
	Details of EVCPs or HPs to be installed are required. Where equipment is not registered in the relevant ENA database, additional information will be required (Section E). A link to the Heat Pump Database can be found on the Databases page on the ENA website1. Type tested V2G EVCPs can be found in the ENA Type Test Verification Report Register. 

	Existing devices at the premises
	Details of any existing EVCPs, electric heating, battery storage, generation (e.g. solar PV), storage or other large load drawing devices. 

	Maximum demand (MD)
	A load survey is required to calculate the Maximum Demand. This should comprise the existing Maximum Demand of the whole premises and the new equipment to be installed as well as any import or load limiting devices. Further Guidance on such devices is available in the FAQ section of the Connecting to the networks page on the ENA website1.

	Supply Capacity / cut-out rating 
	If the cut-out rating is unknown or uncertain, it can be established by asking the DNO. The supply capacity MUST be confirmed with the DNO where the MD is greater than the cut-out rating or where the new MD is >60A per phase (13.8kVA single phase) for residential / non-CT metered premises.  

If the cut-out rating is unknown, a photograph can be provided to the DNO together with the application. Please note that you MUST NOT open the cut-out unless authorised to do so. Further Guidance on cut-out ratings is available on the ENA website1. 

	Adequacy of supply
	An ‘adequacy of supply’ assessment is required prior to installing a EVCP or HP. The DNO must be contacted in advance of installation where there is an identified issue with adequacy or a safety concern with the premises existing DNO service equipment. 


Timelines
Providing that this form is fully and correctly completed, the following timeframes are applicable.
	Notifications
	Provided the installation meets all the relevant notification criteria (i.e. all the applicable checkboxes in Section B that are relevant to the installation can be ticked) installers can connect the new EVCP of HP and notify the DNO using this form within 28 days of their installation.

	Application (60A < MD ≤ 100A)
	The DNO should assess the supply capacity and confirm if the new equipment can be connected within 10 working days of receiving the completed form. 

	Application (MD > 100A)
	The DNO will respond within the timescales as per the Electricity Distribution Licence, Electricity Guaranteed Standards of Performance (GSoP) Regulations 2010
. 


	Declaration 

	Once populated, please remove the cover page, sign below and submit to the relevant DNO with any attachments.

	I confirm that the information I have given in this form is true to the best of my knowledge. If this is for an application for connection, the customer has been advised that the installation may only take place following approval from the DNO. 
	Name:
	……………….

	
	Signature:
	……………….

	
	Date:
	……………….


	Section A – Contact Details

	Installer Contact Details 

	Name
	

	Company
	

	Address line 1
	

	Address line 2
	

	Town
	

	Postcode
	

	Contact Number
	

	Email
	

	If necessary, are we able to contact the customer directly e.g. to arrange a fuse upgrade
	x
	Yes
	☐
	No

	Customer Contact Details

	Name
	

	Contact Number
	

	Email
	

	Installation Location Address 

	Address line 1
	

	Address line 2
	

	Town
	

	Postcode
	


	Section B – Notification Criteria

	All Equipment Types


	☐
	Only connecting one additional piece of equipment (EV Charge Point or Heat Pump)

	
	YES
	DNO cut-out rating known 

	
	YES
	No safety concerns over integrity of DNO service equipment

	
	YES
	No other issues identified with adequacy or integrity of the DNO service equipment

	
	☐
	Not a Looped Service 

	
	YES
	Metered supply

	
	☐
	Maximum Demand less than the known cut-out rating

	
	☐
	Maximum Demand less than 13.8kVA per phase OR the premises is CT metered OR the premises load is limited to below the known cut-out fuse rating

	HP only
	YES
	Heat pump system under single controller only 

	
	YES
	Total heat pump system Maximum Demand ≤32A

	
	YES
	Model marked at ‘Connect and Notify’ in the ENA’s HP Database 

	EVCP only
	☐
	AC Output 

	
	☐
	Premises MD ≤13.8 kVA per phase OR

 where CT metered: Maximum AC output of EV charge points ≤30% of the Maximum Import Capacity

	V2G only
	☐
	Total installed generating capacity (including any PV, storage and V2G storage) ≤3.68kW (16A) per phase and excluding any export limiting device

	
	☐
	V2G EVCP charge point Fully Type Tested and registered in the ENA Type Test Verification Report Register

	Does the installation meet all applicable notification criteria? If yes (i.e., all applicable checkboxes in Section B above are ticked), you can connect the equipment and notify the DNO within 28 days. If no, please apply to the DNO before connecting the equipment.
	☐
	No – Apply to the DNO before installation

	
	x
	Yes – Notify the DNO of the installation 
	Date installed:
	…………

	V2G notify requirements
	☐
	Confirmation that the V2G EVCP was installed and commissioned in accordance with EREC G98
 – this is V2G only

	
	☐
	Electrical schematic of the installation and site layout showing location of the EVCP attached 


	Section C – Electricity Supply Details

	Type of premises
	☐
	Residential house 
	☐
	Residential flat 

	
	☐
	Commercial
	☐
	Public

	
	☐
	Other – Please detail: 
	…………..

	MPAN
 
11-digit MPRN if Northern Ireland
	_ _ – _ _ _ _ – _ _ _ _ – _ _ _

	Smart Meter installed on site
	☐
	Yes
	☐
	No

	Declared Voltage at Connection Point
	
	400
	Volts

	Number of Phases
	☐
	Single Phase
	x
	Three Phase

	
	☐
	Split/two Phase
	
	

	Maximum Demand (MD) of premises
See page 1 for guidance 
	x
	Whole Current Metered 
	………….
	Amps

	
	
	
	
	

	Supply Capacity 

Agreed Supply/Maximum Import Capacity
	x
	Whole Current Metered 
	………….
	Amps per phase

	
	
	
	
	

	Supply capacity confirmed by the DNO? 

Must be confirmed with DNO if MD>60A
	
	
	 
	

	
	x
	No
	
	

	Premises Cut-out Rating

If known. See the cover page for guidance
	Whole Current Metered only
	…………..
	Amps

	Import or load limiting device on premises
	
	Yes 
	If yes, please confirm MD of the premises with load limiting device installed: 
	………….       Amps

	
	x
	No

	G100 export limiting scheme on premises
	☐
	Yes
	Please detail: 
	………….

	
	☐
	No

	Any issues identified with the DNO existing supply equipment?
	
	Yes
	Please detail: 
	………….

	
	x
	No

	Final or Proposed Earthing Arrangements
 
	☐
	TN-C-S (PME)
	☐
	TT (Direct)

	
	☐
	Customer Substation (HV CT metered)
	☐
	TN-S (SNE)



	Is the service looped
? 
	☐
	Yes, multiple service cables present
	☐
	No


	Section D – Existing equipment at premises if applicable (this section is for V2G applications only)

	Technology Type
	Approximate date of installation
	Manufacturer
	Manufacturer’s Ref No. where available
	Registered Capacity (kW)
	Phase (if known)
	Power Factor
	Device to be removed  

	
	
	
	
	Import
	Export
	
	
	

	Example 
	DD/MM/YYYY
	CompanyX
	1234
	3.68
	6.2
	
	
	No

	Heat Pump 
	
	
	
	
	
	
	
	

	EVCP
	
	
	
	
	
	
	
	

	V2G EVCP
	
	
	
	
	
	
	
	

	Solar PV
	
	
	
	
	
	
	
	

	Battery Storage
	
	
	
	
	
	
	
	

	Other (please specify here): 

…………..
	
	
	
	
	
	
	
	


	Section E – Equipment to be installed

	Type of equipment
Tick all that apply (if selecting multiple this must be an application)
	 x
	Heat Pump 

	
	☐
	Electric Vehicle Charge Point (EVCP)

	
	☐
	Vehicle-to-Grid Electric Vehicle Charge Point (V2G EVCP)

	Maximum Current Demand of proposed equipment

Include any associated additional components. The aggregate maximum simultaneous current of all pieces of equipment must be stated. 
	☐
	Single phase
	………
	Amps

	
	x
	Three phase
	11.50
	Amps

	Electric Vehicle Charge Points 

	Manufacturer
	

	Model
	

	Model in the ENA EVCP Database (DC Only)
	☐
	Yes
	Product ID:
	………….

	
	☐
	No
	
	If no, fill in Section F

	V2G Electric Vehicle Charge Points 

	Manufacturer
	

	Model
	

	Export Capacity (kW)
	

	Model Fully Type Tested and registered in the ENA Type Test Verification Report Register
	☐
	Yes
	Product ID:
	………….

	
	☐
	No
	
	If no, fill in Section F

	Heat Pumps

	Manufacturer
	Mitsubishi Electric UK

	Model
	PUZ-WM85YAA

	How will the Heat Pump system be used? 

Please tick one 
	The Heat Pump model stated will provide:
	x
	Heating only

	
	
	☐
	Heating and cooling

	Does the Heat Pump system have additional components installed? 
	Back-up heater:
	Boost Heater:
	Immersion heater:

	
	
	On-board
	
	On-board
	
	On-board

	
	
	External
	
	External
	 x
	External

	Model in the ENA Heat Pump Database 
	 x
	Yes
	Register No:
	HP_0692

	
	
	No
	
	If no, fill in Section F


	Section F – Equipment not currently in ENA Databases 

	EVCP (DC Only)

	You must provide the required data for DC-coupled EVCP models not currently in the ENA EVCP Database. It is the installer’s responsibility to ensure all information required to populate the EVCP Database is provided.

	Datasheet and Power Quality documentation for the EVCP

(Rated power, harmonic emission data & test standard applied for harmonic emission data)
	Must attach with application

	V2G EVCP Only

	If only part of the V2G ECVP is not Fully Type Tested and registered with the ENA Type Test Verification Report Register, Form A2-1 or A2-2 or A2-3 (as appropriate) should be submitted to the DNO with this form. These forms can be downloaded from the ENA website Resource Library: https://www.energynetworks.org/industry-hub/resource-library/

	EREC G98 or G99 Forms A1-3 (where applicable) 
	Must attach with application

	Heat Pumps Only

	You must fill in the following Power Quality details required for non-registered Heat Pump Models. It is the installer’s responsibility to ensure all information required to populate the Heat Pump Database is provided.

	Datasheet and Power Quality documentation for the Heat Pump.
	Must attach with application

	Microgeneration Certificate Scheme
 Product Requirements met
	☐
	Yes
	☐
	No

	Proposed installation complies with:
	Technical requirements of BS EN/IEC 61000-3-2 (harmonics)
	☐
	Yes
	☐
	No

	
	BS EN/IEC 61000-3-12 (harmonics)
	☐
	Yes (Rsce = 33)

	
	
	☐
	Yes, subject to minimum short-circuity power (Ssc)

	
	
	☐
	No

	
	Technical requirements of BS EN/IEC 61000-3-3 (flicker)
	☐
	Yes
	☐
	No

	
	BS EN/IEC 61000-3-11 (flicker)
	☐
	Yes (meets 61000-3-3 tech. requirements) 

	
	
	☐
	Yes, subject to a service current capacity ≥100A per phase

	
	
	☐
	Yes, subject to a Zmax value at point of supply

	
	
	☐
	No
	
	

	Microgeneration Certificate Scheme
 Product Requirements met
	☐
	Yes
	☐
	No

	Proposed installation complies with:
	Technical requirements of BS EN/IEC 61000-3-2 (harmonics)
	☐
	Yes
	☐
	No

	
	BS EN/IEC 61000-3-12 (harmonics)
	☐
	Yes
	☐
	No

	
	Technical requirements of BS EN/IEC 61000-3-3 (flicker)
	☐
	Yes
	☐
	No

	
	BS EN/IEC 61000-3-11 (flicker)
	☐
	Yes
	☐
	No


� � HYPERLINK "https://www.energynetworks.org/operating-the-networks/connecting-to-the-networks" �https://www.energynetworks.org/operating-the-networks/connecting-to-the-networks�


� � HYPERLINK "https://www.energynetworks.org/info/faqs/who-is-my-network-operator.html" �https://www.energynetworks.org/info/faqs/who-is-my-network-operator.html� 


� � HYPERLINK "https://www.ofgem.gov.uk/ofgem-publications/47616/connections-gsop-guidance-sept0809.pdf" �https://www.ofgem.gov.uk/ofgem-publications/47616/connections-gsop-guidance-sept0809.pdf�. See local DNO connections GSoP for specific response timescales in your area.


� G98 and G99 forms are not required in addition to this form – this form replaces the need to fill in G98 and G99 forms for the V2G if “connect and notify” process.


� See � HYPERLINK "https://www.energynetworks.org/operating-the-networks/connecting-to-the-networks" �https://www.energynetworks.org/operating-the-networks/connecting-to-the-networks� for details. If the supply is unmetered, the ‘Apply to Connect’ process is applicable and the local DNO must be contacted.


� As per BS 7671 and the IET Code of Practice: � HYPERLINK "https://www.theiet.org/resources/standards/cop-electric.cfm" �https://www.theiet.org/resources/standards/cop-electric.cfm�


� Some DNO cut-outs have more than one DNO service cable terminated in the DNO cut-out. Such a situation indicates a ‘Looped Service’ where there are one or more services connected via the cut-out.  Note this may impact on the adequacy of the DNO service equipment. Looped services can be found anywhere but are often found in housing estates from the 1970s & 1980s, rural areas and terraced housing.


� Connection of additional equipment or reconfiguration not included in this application is not permitted without submitting another application


� https://www.microgenerationcertification.org/mcs-standards/product-standards/heat-pumps/


� https://www.microgenerationcertification.org/mcs-standards/product-standards/heat-pumps/





